CRITICAL

MASTER THE ATOM

PHASE 1 GAP ANALYSIS

Comprehensive Physics Review

"An error in Phase 1 cascades into every subsequent phase"

Reference: Westinghouse 4-Loop PWR (3411 MWt)

# EXECUTIVE SUMMARY

A thorough review of the Phase 1 physics implementation against real PWR thermal-hydraulics has identified THIRTEEN significant gaps that must be addressed before proceeding. These gaps fall into three categories:

| Category | Gaps Found | Impact |
| --- | --- | --- |
| CRITICAL | 5 gaps | Will cause fundamentally incorrect behavior |
| MAJOR | 5 gaps | Will cause noticeably unrealistic dynamics |
| MINOR | 3 gaps | Will reduce fidelity but not break simulation |

The most critical finding: The pressurizer steam bubble model is fundamentally incomplete. It treats the steam space as a simple polytropic compression volume, but real pressurizer dynamics involve multiple non-equilibrium phenomena that significantly affect pressure response.

# GAP 1: P-T-V Coupling [CRITICAL]

STATUS: Previously identified in Phase 1 Addendum

## The Problem

Original design treats pressure as a constant INPUT to thermal expansion calculations. But thermal expansion in the confined RCS causes pressure changes, which in turn affect water properties.

## Impact

- Expansion calculations will be incorrect by 5-15%

- Pressurizer level changes will be wrong

- Subcooling margin calculations will be inaccurate

## Resolution

Module 7 (CoupledThermodynamics) with iterative solver - ALREADY DOCUMENTED

# GAP 2: Flash Evaporation (Outsurge) [CRITICAL]

STATUS: NOT IN CURRENT DESIGN

## The Problem

When RCS temperature drops or coolant leaves the pressurizer (outsurge), pressure begins to fall. The saturated water in the pressurizer will FLASH (spontaneously boil) to maintain saturation conditions. This is a critical self-regulating mechanism.

## Real Physics

// During outsurge, pressure drops

// Water at saturation FLASHES to steam

// Flashing RETARDS pressure drop (self-regulating)

// Flash rate depends on:

//  - Rate of pressure decrease

//  - Water superheat relative to new saturation temp

//  - Available thermal energy in liquid

m_flash = (dP/dt) * V_liquid * ρ_f / h_fg

## Current Design Deficiency

The current SteamThermodynamics module has NO flash evaporation model. It assumes the steam volume changes only from surge flow - but in reality, mass is TRANSFERRED from liquid to steam during depressurization.

## Impact

- Outsurge transients will show pressure dropping TOO FAST

- Heaters will appear less effective than they should be

- Loss of subcooling events will occur prematurely

## Required Addition

public static float FlashEvaporationRate(

float pressure_psia,

float dP_dt,           // psia/sec (negative for depressurization)

float liquidVolume_ft3,

float liquidTemp_F) {

float T_sat = WaterProperties.SaturationTemperature(pressure_psia);

float superheat = liquidTemp_F - T_sat; // Should be ~0 at saturation

float h_fg = WaterProperties.LatentHeat(pressure_psia);

float rho_f = WaterProperties.WaterDensity(T_sat, pressure_psia);

// Flash rate proportional to depressurization rate

if (dP_dt >= 0) return 0f; // No flashing during pressurization

float m_dot = -dP_dt * liquidVolume_ft3 * rho_f * CP_WATER / h_fg;

return m_dot; // lb/sec of steam produced

}

# GAP 3: Spray Condensation Dynamics [CRITICAL]

STATUS: OVERSIMPLIFIED IN CURRENT DESIGN

## The Problem

Spray condensation is NOT instantaneous. Cold spray droplets (~558°F from cold leg) enter the saturated steam space (~653°F at 2250 psia). Heat transfer occurs over a finite time as droplets fall through the steam space.

## Real Physics

- Spray water enters at ~558°F (Tcold)

- Steam in pressurizer is at ~653°F (Tsat at 2250 psia)

- ΔT for heat transfer = ~95°F

- Droplet residence time ~0.5-2 seconds

- Not all spray may condense before reaching liquid surface

- Spray pattern affects effectiveness (nozzle design)

## Current Design Deficiency

The current model assumes spray instantly condenses steam. In reality:

// WRONG (current approach)

dP_spray = -K * sprayFlow; // Instant pressure drop

// CORRECT (should be)

// 1. Calculate heat transfer to droplets

// 2. Calculate steam condensed on droplets

// 3. Account for residence time

// 4. Steam mass balance affects pressure

## Impact

- Spray appears MORE effective than reality during fast transients

- Pressure oscillations may be unrealistically damped

- Spray valve sizing/capacity will seem wrong

## Required Model

public struct SprayDynamics {

public float dropletMass;       // lb in flight

public float dropletTemp;       // °F average

public float condensationRate;  // lb/sec

}

public static float SprayCondensationRate(

float sprayFlow_gpm,

float sprayTemp_F,      // From cold leg

float steamTemp_F,      // Tsat in pressurizer

float steamPressure_psia) {

float h_fg = WaterProperties.LatentHeat(steamPressure_psia);

float deltaT = steamTemp_F - sprayTemp_F;

float cp = WaterProperties.WaterSpecificHeat(sprayTemp_F, steamPressure_psia);

// Energy available to condense steam

float sprayMassFlow = sprayFlow_gpm * 8.33f / 60f; // lb/sec

float Q_available = sprayMassFlow * cp * deltaT; // BTU/sec

// Steam condensed (limited by spray capacity)

float m_condensed = Q_available / h_fg;

return m_condensed; // lb/sec

}

# GAP 4: Wall Condensation [MAJOR]

STATUS: NOT IN CURRENT DESIGN

## The Problem

The pressurizer vessel wall acts as a thermal mass. During insurge transients, steam can condense on the cooler upper walls. During outsurge, heat stored in the walls can cause additional flashing.

## Real Physics

// Wall condensation occurs when:

// T_wall < T_sat (steam condenses on wall)

// Wall heat transfer:

Q_wall = h_conv * A_wall * (T_sat - T_wall)

// For Westinghouse 4-loop pressurizer:

// - Wall thickness: ~4.5 inches

// - Wall mass: ~200,000 lb

// - Wall thermal mass: ~24,000 BTU/°F

## Impact

- Insurge transients show pressure rising TOO FAST initially

- Long-term pressure drift may be wrong

- Wall 'memory' effects from previous transients missing

## Required Model

public static float WallCondensationRate(

float wallTemp_F,

float steamTemp_F,

float steamPressure_psia,

float wallArea_ft2 = 560f) {  // Westinghouse 4-loop

if (wallTemp_F >= steamTemp_F) return 0f;

float h_conv = 200f; // BTU/hr·ft²·°F (condensing)

float h_fg = WaterProperties.LatentHeat(steamPressure_psia);

float Q = h_conv * wallArea_ft2 * (steamTemp_F - wallTemp_F) / 3600f;

return Q / h_fg; // lb/sec condensed

}

# GAP 5: Rainout (Bulk Condensation) [MAJOR]

STATUS: NOT IN CURRENT DESIGN

## The Problem

'Rainout' is bulk condensation of steam in the vapor space that forms droplets which fall back to the liquid surface. This occurs when the vapor becomes locally supersaturated.

## When Rainout Occurs

- After spray operation - mixes subcooled spray with steam

- When wall condensation cools adjacent steam

- During rapid depressurization when steam becomes subcooled

## Impact

- Pressure recovery after spray may be too fast

- Steam inventory calculations may drift

## Required Model

public static float RainoutRate(

float steamTemp_F,

float saturationTemp_F,

float steamMass_lb) {

// Rainout occurs when steam is subcooled

float subcooling = saturationTemp_F - steamTemp_F;

if (subcooling <= 0) return 0f;

// First-order decay toward equilibrium

float tau = 30f; // seconds (characteristic time)

return steamMass_lb * subcooling / (tau * 10f);

}

# GAP 6: Non-Equilibrium Three-Region Model [CRITICAL]

STATUS: FUNDAMENTAL ARCHITECTURE ISSUE

## The Problem

The current design uses a simplified two-phase equilibrium model. Real pressurizer dynamics require a NON-EQUILIBRIUM model with at least THREE regions:

| Region | Contents | State |
| --- | --- | --- |
| 1. Upper Vapor | Saturated steam + spray droplets | May be superheated or subcooled |
| 2. Saturated Liquid | Water at saturation | At Tsat, flashing/condensing |
| 3. Subcooled Liquid | Surge water from hot leg | Below Tsat, mixing with region 2 |

## Why This Matters

During an insurge:

- Subcooled water (~619°F from hot leg) enters at bottom

- This water is BELOW saturation temp (~653°F)

- It must be heated by the saturated liquid before equilibrium

- This creates stratification and delays pressure response

During an outsurge:

- Water leaves from surge line at bottom

- Flashing occurs at liquid surface (not in bulk)

- Interface area affects flash rate

## Required Architecture Change

public struct PressurizerState {

// Region 1: Vapor

public float vaporMass;        // lb

public float vaporTemp;        // °F (may differ from Tsat)

public float vaporVolume;      // ft³

// Region 2: Saturated Liquid

public float satLiquidMass;    // lb

public float satLiquidTemp;    // °F (= Tsat)

// Region 3: Subcooled Liquid (from surge)

public float subLiquidMass;    // lb

public float subLiquidTemp;    // °F (< Tsat)

// Wall

public float wallTemp;         // °F

// System

public float pressure;         // psia (common to all regions)

}

# GAP 7: Heater Thermal Dynamics [MAJOR]

STATUS: OVERSIMPLIFIED

## The Problem

Pressurizer heaters don't instantly add heat to the water. They must first heat their own thermal mass, then transfer heat to the surrounding water.

## Westinghouse 4-Loop Heater Specifications

| Parameter | Value |
| --- | --- |
| Total heater power | 1800 kW |
| Proportional heaters | ~500 kW (modulating) |
| Backup heaters | ~1300 kW (on/off banks) |
| Heater surface temp limit | ~800°F (to prevent burnout) |
| Time constant | ~10-30 seconds |

## Required Model

public struct HeaterState {

public float propPower;     // kW (0-500)

public float backupPower;   // kW (0-1300)

public float surfaceTemp;   // °F

public float effectivePower; // kW after thermal lag

}

void UpdateHeaters(ref HeaterState h, float setpoint, float dt) {

// Proportional control

h.propPower = Clamp((setpoint - pressure) * K_prop, 0, 500);

// Thermal lag - heaters don't respond instantly

float tau = 15f; // seconds

h.effectivePower += (h.propPower + h.backupPower - h.effectivePower) * dt / tau;

}

# GAP 8: Surge Line Hydraulics [MAJOR]

STATUS: NOT MODELED

## The Problem

The surge line connecting the pressurizer to the hot leg has significant hydraulic resistance and thermal lag. Flow through it is not instant.

## Westinghouse 4-Loop Surge Line

| Parameter | Value |
| --- | --- |
| Diameter | 10-14 inches |
| Length | ~40-60 feet |
| Volume | ~50-80 ft³ |
| Friction losses | ~2-5 psi at max surge |
| Max surge rate | ~200-400 ft³/min |

## Impact

- Instantaneous pressure transmission is assumed but doesn't occur

- Surge line acts as low-pass filter on RCS transients

- Temperature of surge water depends on recent history

## Required Model

public static float SurgeLineFlow(

float P_rcs, float P_pzr,

float T_hotleg_F, float P_psia) {

float deltaP = P_rcs - P_pzr;

float rho = WaterProperties.WaterDensity(T_hotleg_F, P_psia);

// Hydraulic model: Q = K * sqrt(deltaP * rho)

float K = 150f; // gpm/sqrt(psi·lb/ft³) - tune to plant

float Q = K * Mathf.Sign(deltaP) * Mathf.Sqrt(Mathf.Abs(deltaP) * rho);

return Q; // gpm

}

# GAP 9: Enthalpy Transport [MAJOR]

STATUS: NOT EXPLICITLY TRACKED

## The Problem

The current design tracks temperature and volume but not ENTHALPY explicitly. For accurate transient response, enthalpy (h) must be tracked for:

- Surge water entering pressurizer (from hot leg: ~619°F)

- Spray water entering pressurizer (from cold leg: ~558°F)

- Water leaving pressurizer (at saturation: ~653°F)

## Why Enthalpy Matters

// Insurge: hot water enters, BUT it's still subcooled!

T_hotleg = 619°F

T_sat(2250) = 653°F

h_surge = h_f(619°F) ≈ 640 BTU/lb

h_sat = h_f(653°F) ≈ 700 BTU/lb

// Energy deficit: 60 BTU/lb must come from somewhere!

// This is why insurge initially DROPS pressure slightly

// before thermal equilibrium is reached.

## Required Model

public static float SurgeEnthalpyEffect(

float surgeFlow_gpm,       // + = insurge

float surgeTemp_F,

float pzrSatTemp_F) {

float h_surge = WaterProperties.Enthalpy(surgeTemp_F, 2250f);

float h_sat = WaterProperties.Enthalpy(pzrSatTemp_F, 2250f);

float massFlow = surgeFlow_gpm * 8.33f / 60f; // lb/sec

return massFlow * (h_surge - h_sat); // BTU/sec deficit/surplus

}

# GAP 10: Steam Table Resolution Near Saturation [MINOR]

STATUS: MAY CAUSE NUMERICAL ISSUES

## The Problem

Properties near the saturation line change RAPIDLY. Small interpolation errors near saturation can cause:

- Incorrect determination of subcooled vs. saturated state

- Numerical oscillations in iterative solvers

- Wrong phase determination during transients

## Recommendation

Use piecewise polynomial fits optimized for the operating range (2000-2500 psia), not general-purpose correlations that work across entire range.

# GAP 11: Missing Liquid Enthalpy Function [MINOR]

STATUS: NOT IN CURRENT API

## The Problem

WaterProperties has density, specific heat, thermal expansion - but NO explicit enthalpy function. Enthalpy is needed for energy balances.

## Required Addition

public static float WaterEnthalpy(float tempF, float pressurePsia) {

// h = h_ref + ∫Cp dT (approximately)

float T_ref = 32f; // °F

float h_ref = 0f;  // BTU/lb at 32°F

float Cp_avg = WaterSpecificHeat((tempF + T_ref) / 2f, pressurePsia);

return h_ref + Cp_avg * (tempF - T_ref);

}

public static float SteamEnthalpy(float tempF, float pressurePsia) {

float h_f = WaterEnthalpy(SaturationTemperature(pressurePsia), pressurePsia);

float h_fg = LatentHeat(pressurePsia);

return h_f + h_fg; // For saturated steam

}

# GAP 12: Steam Quality / Void Fraction [MINOR]

STATUS: NOT MODELED

## The Problem

In the pressurizer, steam 'quality' (fraction that is vapor) and void fraction are important for level calculation. The liquid surface has a 'frothy' transition zone.

## Impact

- Level indication may not match actual liquid mass

- Heat transfer at interface depends on void fraction

# GAP 13: Westinghouse 4-Loop Reference Values [CRITICAL]

STATUS: SOME VALUES MISSING OR IMPRECISE

## Required Reference Parameters

| Parameter | Westinghouse 4-Loop | In Current Design? |
| --- | --- | --- |
| Pressurizer total volume | 1800 ft³ | ✓ Yes |
| Normal liquid volume | ~1080 ft³ (60%) | ✓ Yes |
| Normal steam volume | ~720 ft³ (40%) | ✓ Yes |
| Heater power | 1800 kW | ✓ Yes |
| Spray flow capacity | ~900 gpm max | ⚠ Check |
| Surge line diameter | 10-14 inches | ✗ Missing |
| Surge line length | ~50 feet | ✗ Missing |
| Wall thickness | ~4.5 inches | ✗ Missing |
| Wall mass | ~200,000 lb | ✗ Missing |
| PORV setpoint | 2335 psig | ✓ Yes |
| Safety valve setpoint | 2485 psig | ✓ Yes |
| Spray line diameter | ~4 inches | ✗ Missing |
| Normal operating pressure | 2235 psig | ✓ Yes |
| Spray temperature | ~558°F (Tcold) | ⚠ Implicit |
| Surge water temperature | ~619°F (Thot) | ⚠ Implicit |

# SUMMARY: REQUIRED PHASE 1 CHANGES

## New Modules Required

1. CoupledThermodynamics.cs (already documented)

2. PressurizerPhysics.cs - Contains flash, spray, wall, rainout models

3. HeatTransfer.cs - Enthalpy functions, heat transfer coefficients

## Existing Module Updates

1. WaterProperties.cs - Add Enthalpy(), improve near-saturation accuracy

2. SteamThermodynamics.cs - Add mass balance functions

3. PhysicsConstants.cs - Add Westinghouse 4-loop reference values

## Updated Test Count

| Module | Original | Updated |
| --- | --- | --- |
| WaterProperties | 17 | 22 (+enthalpy, quality) |
| SteamThermodynamics | 6 | 12 (+mass balance) |
| CoupledThermodynamics | 10 | 10 (new) |
| PressurizerPhysics | 0 | 18 (new - flash, spray, wall, rainout) |
| HeatTransfer | 0 | 8 (new - enthalpy transport) |
| ThermalMass | 4 | 6 (+wall thermal mass) |
| ThermalExpansion | 5 | 5 (uses coupled solver) |
| ReactorKinetics | 8 | 8 (unchanged) |
| FluidFlow | 5 | 8 (+surge line) |
| Integration Tests | 5 | 15 (+pressurizer transients) |
| TOTAL | 60 | 112 |

## Estimated Additional Time

These gaps add approximately 1-2 weeks to Phase 1 timeline.

However, getting this RIGHT in Phase 1 will save MONTHS of debugging in Phases 3-6.

# PHASE 1 REVISED EXIT GATE

ALL of the following must pass before proceeding to Phase 2:

| Gate Requirement | Status |
| --- | --- |
| All 112 unit tests passing | □ PASS □ FAIL |
| Coupled P-T-V solver converges in <20 iterations | □ PASS □ FAIL |
| Flash evaporation rate matches literature (~within 20%) | □ PASS □ FAIL |
| Spray condensation rate realistic (~within 20%) | □ PASS □ FAIL |
| Wall thermal mass included and validated | □ PASS □ FAIL |
| Enthalpy functions validated against steam tables | □ PASS □ FAIL |
| 10°F Tavg rise → ~60-80 psi pressure rise | □ PASS □ FAIL |
| Insurge transient shows correct dynamics | □ PASS □ FAIL |
| Outsurge transient shows flash effect | □ PASS □ FAIL |
| All Westinghouse reference values documented | □ PASS □ FAIL |
| Code review completed | □ PASS □ FAIL |
| PHASE 1 GATE APPROVED | □ YES □ NO |

This gap analysis ensures Critical will have physics that matches a real Westinghouse 4-loop PWR.